## Sheet
Sheet Name | Description
J23-0064-ITC-009-01 | nan: Process Operator Sequence

## J23-0064-ITC-009-01
J23-0064-ITC-009-01
|  |  | Commissioning |  | Revision: | A
|  |  | Process Operator Sequence |  | Template: | ITC_Type
[5 empty] | Project: | MAC TLO HPU Upgrade
[5 empty] | Date: | 29/11/23
Operator Sequence
Test Number | Test Description | Pre-Requisites | Test Action | Expected Result | Pass | Comment
1 | Set Test Conditions |  | From HMI Engineering Menu: Set Surface 1" Hose Treatment Set Points == Set SO3 Maximum pH Correction Time == Set SO3 Minimum pH Correction Time == Set NH3 Maximum pH Correction Time == Set NH3 Minimum Correction Time == |  |  | Assume a pre-requisite for all tests is that trips have been cleared unless otherwise stated.
2 | Pre-Treatment: Air Preheat |  | From Operator Actions menu: Select 'Start Air Pre Heater' | Preheat running status shown. Preheat Status shows complete once time has elapsed and EHS655 has reached 480.0°C |  | Allow upstream flow to ramp before simulation temperature starts increasing and preheat timer begins decreasing.
3 | Pre-Treatment: Stop Preheat | Air Preheater running | From Operator Actions menu: Select 'Stop Air Pre Heater' | Preheat offline status shown. Remaining time indication resets.
4 | Pre-Treatment: Set Hose Type |  | From Operator Actions menu: Select 'Set Hose Type' Set Surface 1" | 'Hose Type' indication reflects selection. |  | Surface 1" selected so shortened test set points are used.
5 | Pre-Treatment: Set Number of Hose Pairs |  | From Operator Actions menu: Select 'Set Number of Hose Pairs' On Subsequent popup choose number of hose pairs to be tested | Hose Pairs Selected' indication reflects number chosen. Hose Treatment and coupling test matrices displays chosen number of hose pair rows
6 | Hose Connection Verification: Start | ZS540 == 1 ZS541 == 1 ZS542 == 1 | From Operator Actions OR Hose Coupling Verification Screen: Select 'Start Hose Coupling Verification Test' Select ' Confirm' on subsequent popup | Confirmation popup is shown THEN Hose Coupling Verification screen is shown AND test running indication is shown on this screen. After a few seconds, progress should be observed in the test matrix.
7 | Hose Connection Verification: Cancel | Hose Connection Verification Test Running | From Operator Actions OR Hose Coupling Verification Screen: Select 'Cancel Hose Coupling Verification Test' Select 'Confirm' on subsequent popup | Confirmation popup is shown THEN Test Status shows offline.
8 | Hose Connection Verification: Trip | Hose Connection Verification Test Running | Activate a trip (Estop) | Test Status shows offline Test matrix does not progress. |  | Repeat test for trips: 500, 501
9 | Hose Connection Verification: Resume | Hose Connection Verification Test Running then Stopped or Tripped | Observe progress of test on test matrix. From Operator Actions OR Hose Coupling Verification Screen: Select 'Stop Hose Coupling Verification Test' Select ' Confirm' on subsequent popup | Test restarts from the beginning. Test Status shows running
10 | Hose Connection Verification: Successful Conditions | ZS540 == 1 ZS541 == 1 ZS542 == 1 Hose Pairs correctly connected | Start Hose Coupling Verification Test. Observe that the Continuity test for the current hose passes (corresponding box turns green) Observe that the leak test for the current hose passes Observe that the Test complete box turns green for the corresponding hose pair. | After completion of the test actions for each hose pair selected, test status shows: Offline Complete Passed Correct valves status is observed throughout sequence progression
11 | Hose Connection Verification: Continuity Fail | ZS540 == 1 ZS541 == 1 ZS542 == 1 Hose Pair Coupling Disconnected | Start Hose Coupling Verification Test. Observe that the Continuity test for the test hose fails (corresponding box turns orange) Observe that the leak test for the test hose passes Observe that the Test complete box turns green for the corresponding hose pair. | After completion of the test actions for each hose pair selected, test status shows: Offline Complete Failed Correct valves status is observed throughout sequence progression
12 | Hose Connection Verification: Leak Fail | ZS540 == 1 ZS541 == 1 ZS542 == 1 Leaky Hose Connected | Start Hose Coupling Verification Test. Observe that the Continuity test for the test hose passes Observe that the leak test for the test hose fails | After completion of the test actions for each hose pair selected, test status shows: Offline Complete Failed Correct valves status is observed throughout sequence progression |  | Test with one leaky hose out of the pair.
13 | Hose Treatment: Start | Hose Verification Complete Air Preheat Complete | From Operator Actions menu or Treatment Matrix screen: Select 'Start Hose Treatment' Select ' Confirm' on subsequent popup | SO3 & NH3 Preparation indication shows running.
14 | Hose Treatment: Abort | Hose Treatment Started | From Operator Actions menu or Treatment Matrix screen: Select 'Abort Hose Treatment' Select ' Confirm' on subsequent popup | Treatment matrix and hose coupling verification are reset.
15 | Hose Treatment: Pause | Hose Treatment Running | From Operator Actions menu or Treatment Matrix screen: Select 'Pause Hose Treatment' Select ' Confirm' on subsequent popup | Treatment indication shows paused. Treatment Matrix does not progress. SO3 and NH3 manufacture show incomplete. On -Pause Air Purge indication given.
16 | Hose Treament: Trip | Hose Treatment Running | Activate a trip (Estop) | Treatment indication shows paused. Treatment Matrix does not progress. SO3 and NH3 manufacture show incomplete
17 | Resume Hose Treatment | Hose Treatment Started THEN Paused or Tripped | Start Hose Treatment | Hose Treatment should resume from the step which was in progress prior to cancellation. |  | Allow Hose Treatment Sequence to progress past first matrix entry before cancellation.
18 | Hose Treatment Sequence: Successful Conditions | Hose Verification Complete Air Preheat Complete AT321 within normal range (~7) LT320 within normal range (<50) | Start Hose Treatment | Test matrix and timers progress, reflective of the functional description and batch logic documentation. After Treatment Matrix finishes, 'End Campaign' button becomes active (coloured) Correct valves status is observed throughout sequence progression
19 | Hose Treatment Sequence: Pre Water Flush pH Correction | AT321 > 8.5 or AT321 < 6.0 | Start Hose Treatment. Confirm the 'Water Flush' step does not become active when the treatment sequece reaches it, and that the pH correction becomes active. After some delay observe that the 'Water Flush' Step proceeds as normal. | Test matrix and timers progress, reflective of the functional description and batch logic documentation. After Treatment Matrix finishes, 'End Campaign' button becomes active (coloured) Correct valves status is observed throughout sequence progression
20 | Hose Treatment Sequence: Pre Water Flush Waste Water discharge | LT320 > 50.0 | Start Hose Treatment. Confirm the 'Water Flush' step does not become active when the treatment sequece reaches it, and that both WW.21.01 & HS328 become active. Once LT320 reads below 50%, observe that the 'Water Flush' proceeds as normal. | Test matrix and timers progress, reflective of the functional description and batch logic documentation. After Treatment Matrix finishes, 'End Campaign' button becomes active (coloured) Correct valves status is observed throughout sequence progression
21 | Hose Treatment Sequence: Post Treatment pH correction. |  | Start Hose Treatment. Allow Treatment Matrix to progress through to when Water Flush is active. Set AT321 above High range or below Low range. Allow treatment matrix to complete and observe that the treatment status remains incomplete and pH correction is running. After some delay observe that the 'Water Flush' Step proceeds as normal. | Test matrix and timers progress, reflective of the functional description and batch logic documentation. After Treatment Matrix finishes, 'End Campaign' button becomes active (coloured) Correct valves status is observed throughout sequence progression.
22 | End of campaign - Continue Processing | Hose Treatment Sequence complete. | Operate ' End Campaign' Button. On subsequent popup select 'Continue Batch Processing' | 'Hose Treatment Completed' popup is displayed as expected. On Operator Actions screen preheat status shows running AND both scrubber indications show stopped. Treatment Matrix is reset to default, Coupling shows incomplete, SO3 and NH3 manufcaturing show incomplete.
23 | End of campaign - Flush Equipment | Hose Treatment Sequence complete. LT303 above low low alarm condition. | Operate ' End Campaign' Button. | 'Hose Treatment Completed' popup is displayed as expected. On Operator Actions screen preheat status shows offline AND end of campaign flush status shows required. Treatment Matrix is reset to default, Coupling shows incomplete, SO3 and NH3 manufcaturing show incomplete. Air preheat status reset.
24 | Equipment Flush:Successful Conditions | Equipment Flush Required is shown on operator actions page. Start Equipment Flush button is active. | Operate 'Start Equipment Flush' Button | On Post Treatment Sequence Status page, Sequence progresses as expected. Upon completion, Equipment Flush required status is cleared. Start Preheat button is re-enabled
25 | Equipment Flush: Stop | Equipment Flush Active | Operate 'Stop Equipment Flush' Button | Equipment Flush status shows stopped. Flush Timers reset on Post Treatment Sequence Status Page.
26 | Equipment Flush: Trip | Equipment Flush Active | Activate a trip | Equipment Flush status shows stopped. Flush Timers reset on Post Treatment Sequence Status Page.
27 | SO3 & NH3 Scrubbers: Start | Air Preheat Complete Hose Coupling Verification Complete | Start Hose Treatment On Subsequent opoup select 'End Campaign' On Operator Actions screen, observe that the 'Start Flush' button is active. Operate the 'Start Flush' button and confirmation | On Operator Actions page, SO3 scrubber and NH3 scrubber indications show running.
28 | SO3 & NH3 Scrubbers: During Pause | Hose Treatment (and scrubbers by extension) running. | Pause Hose Treatment | On Operator Actions page, SO3 scrubber and NH3 scrubber indications show running.
29 | SO3 & NH3 Scrubbers: Trip and Restart | Hose Treatment (and scrubbers by extension) running. | Activate a trip. Observe on Operator Actions page, SO3 scrubber and NH3 scrubber indications show offline. Start Hose Treatment. | On Operator Actions page, SO3 scrubber and NH3 scrubber indications show running. |  | Repeat test for trips: 500, 501
30 | pH Correction: Permissive | FSL315 ==1 AT321 > 8.5 or AT321 < 6.0 | Start Hose Treatment. Confirm the 'Water Flush' step does not become active when the treatment sequece reaches it, and that the pH correction remains offline. Set FSL315 == 0 Observe that pH Correction becomes Active Set FSL315 == 1 Observe that pH Correction becomes Inactive Set FSL 315==1 Observe that pH Correction restarts Set AT321 to normal range (7). After some delay observe that the 'Water Flush' Step proceeds as normal. | FSL315 Alarm is activated when FSL315 = 1. pH Correction Starts After FSL315 is reset. Test matrix and timers progress, reflective of the functional description and batch logic documentation. After Treatment Matrix finishes, 'End Campaign' button becomes active (coloured) Correct valves status is observed throughout sequence progression
Inspection Passed Sign Off
Date:
Beyond Electrical Engineering |  | Name: |  | Signature:
Client |  | Name: |  | Signature:
Remarks or Remedial Action Required:
Remedial Action Completed: